## Data
Item Name | Description | Serial Number | Date | Quantity | Remarks
11.99.40.2619 | Instrument Data sheet for H2S | 1 |  | 1
ADCO | Trans. No. CTA��6.02/EC10870/f E-241 i.-, � �!f,f
D11tc: | ----� •
Form | IDC1, Rev 07 - 26.09.98
OIL | OPERATIONS CT A/15606.02/EC10870/AE-241/8945
6ALSA | ABU DHABI COMPANY FOR ONSHORE CTA/15606.02/EC10870/AE-241/8945
11.99.40.2619 | Instrument Data sheet for H2S |  |  | 1
PROJECT | NO : P11569
EPC | FOR BAB FAR NORTH C02 INJECTION PILOT PROJECT
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S GAS DETECTOR
ORIGINATOR | tqca TYCO PROJ |  |  |  | No.: ALSA JOB No. AE 241
fir, | & Security UAE lLC CA150270
L\ALSA | TYCO DOC. No.: |  |  |  | TFS-D- CA150270-007 _REV.3 Contract No: '',I,•,\ -, ·.
11.99.40.2619 | PROJ. No: P11569 Page of | 13 |  | 1
3.1 | H2S GAS DETECTOR |  |  |  | 5
11.99.40.2619 | Project No.: P11569
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S
The | purpose of this |  |  |  | document is to provide the detailed data sheet for the H2S Gas Detector that
TYCO | Fire & Security |  |  |  | UAE LLC is supplying for EPC for Bab Far North C02 Injection Pilot Project.
Bab | Far North C02 Injection Project.
Vendor | M/s. Tyco Fire |  |  |  | & Security UAE L.L.C
H2S | Hydrogen Sulfide
fl/co | TYCO DOC. NO.: |  |  |  | TFS-D- CA150270-007_REV.3 Page 3 of 13 Project No.: P11569
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S
11.99.52.1620 | MATERIAL REQUISITION FOR FIRE
11.99.40.1611 | DATASHEET FOR FIRE & GAS
11.99.40.2619 | Project No.: P11569
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S
3.1 | H2S GAS DETECTOR
Product | description and specifications |  |  |  | of the H2S Gas Detector is given below:
2 | EQUIPMENT H2S GAS |  |  |  | DETECTOR
4 | HAZARDOUS AREA Ex d IIB+H2, T5 Gb CLASSIFICATION
7 | DETECTOR METHOD ADSORPTION
9 | INSTRUMENT RANGE 0-50 |  |  |  | ppm
DETECTOR | DATA 11 REPEATABILITY |  |  |  | APPLIED GAS,
12 | RESPONSE TIME T50 < 30 sec
� | DOCUMENT TITLE: Project No.: P11569
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S REV.1 Date: 06-08-2015 GAS DETECTOR
P,ii() | tqca TYCO DOC. |  |  |  | NO.: TFS-D- CA 150270-007 _REV.3 Page 5 of 13
20 | LOCAL DISPLAY THREE-DIGIT LED
ELECTRICAL | 3 x M20 VIA NPT %" TO
REQUIREMENT | M20 DUAL CERTIFIED 25 CABLE ENTRY NICKEL PLATED BRASS
EN50270, | EN61000-6-4
� | DOCUMENT TITLE: Project No.: P11569
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S REV. 1 Date: 06-08-2015 GAS DETECTOR
p,,�C) | tuco TYCO DOC. |  |  |  | NO.: TFS-0- CA150270-007 _REV.3 Page 6 of 13
NPT | %" TO M20 DUAL
SPLASH | GUARD-1No/unit
41 | DETECTOR MODEL NUMBER |  |  |  | S4000TH-5-0-12-6
1) | SS316 TAG PLATE SHALL BE PROVIDED LOOSELY & MANUFACTURER'S NAME
1 | 11-76-XTGD-5401-01 TOXIC GAS |  |  |  | DETECTOR- BLOCK VALVE
STATION-1 | MAIN VALVE
2 | 11-76-XTGD-5401-02 TOXIC GAS |  |  |  | DETECTOR- BLOCK VALVE
STATION-1 | BYPASS LINE
3 | 11-76-XTGD-5401-05 TOXIC GAS |  |  |  | DETECTOR- BLOCK VALVE
STATION-1 | MAIN VALVE
4 | 11-76-XTGD-5402-01 TOXIC GAS |  |  |  | DETECTOR- BLOCK VALVE
STATION-2 | MAIN VALVE
5 | 11-76-XTGD-5402-02 TOXIC GAS |  |  |  | DETECTOR- BLOCK VALVE
STATION-2 | BYPASS LINE
6 | 11-76-XTGD-5402-05 TOXIC GAS |  |  |  | DETECTOR- BLOCK VALVE
STATION-2 | MAIN VALVE
7 | 11-71-XTGD-1055W-10 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
� | DOCUMENT TITLE: Project No.: P11569
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S REV. 1 Date: 06-08-2015 GAS DETECTOR
"'ii() | tuca TYCO DOC. |  |  |  | NO.: TFS-D-CA150270-007_REV.3 Page 7 of 13
8 | 11-71-XTGD-1055W-11 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
9 | 11-71-XTGD-1055W-12 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
10 | 11-71-XTGD-1055W-03 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
11 | 11-71-XTGD-1055W-04 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
12 | 11-71-XTGD-1055W-13 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
13 | 11-71-XTGD-1055W-14 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1055
14 | 11-71-XTGD-1054W-01 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1054
15 | 11-71-XTGD-1054W-02 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1054
16 | 11-71-XTGD-1054W-07 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1054
17 | 11-71-XTGD-1054W-08 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK 1054
18 | 11-71-XTGD-1052P-01 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK
19 | 11-71-XTGD-1052P-02 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK
20 | 11-71-XTGD-1052P-03 TOXIC GAS |  |  |  | DETECTOR- EAST FLANK
21 | 11-71-XTGD-1051 P-01 TOXIC |  |  |  | GAS DETECTOR- NORTH FLANK
22 | 11-71-XTGD-1051 P-02 TOXIC |  |  |  | GAS DETECTOR- NORTH FLANK
23 | 11-71-XTGD-1046W-03 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
24 | 11-71-XTGD-1046W-04 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
25 | 11-71-XTGD-1051 P-03 TOXIC |  |  |  | GAS DETECTOR NORTH FLANK
26 | 11-71-XTGD-1046W-14 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
27 | 11-71-XTGD-1046W-15 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
28 | 11-71-XTGD-1046W-16 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
29 | 11-71-XTGD-1046W-17 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
� | DOCUMENT TITLE: Project No.: P11569
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S REV. 1 GAS DETECTOR Date: 06-08-2015
P.�0 | tuco TYCO DOC. |  |  |  | NO.: TFS-D- CA 150270-007 REV.3
30 | 11-71-XTGD-1046W-18 TOXIC GAS |  |  |  | DETECTOR- NORTH 1046 PIG
31 | 11-71-XTGD-1046W-19 TOXIC GAS |  |  |  | DETECTOR- NORTH 1046 PIG
32 | 11-71-XTGD-1046W-20 TOXIC GAS |  |  |  | DETECTOR- NORTH 1046 PIG
33 | 11-71-XTGD-1046W-21 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
34 | 11-71-XTGD-1046W-22 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
35 | 11-71-XTGD-1046W-05 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
36 | 11-71-XTGD-1046W-06 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
37 | 11-71-XTGD-1053W-01 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
38 | 11-71-XTGD-1053W-02 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
39 | 11-71-XTGD-1053W-07 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
40 | 11-71-XTGD-1053W-08 TOXIC GAS |  |  |  | DETECTOR- NORTH FLANK
41 | 11-18-XTGD-5403-14 TOXIC GAS |  |  |  | DETECTOR- NEAR
42 | 11-18-XTGD-5403-15 TOXIC GAS |  |  |  | DETECTOR- NEAR
43 | 11-18-XTGD-5403-16 TOXIC GAS |  |  |  | DETECTOR- NEAR MANIFOLD
44 | 11-18-XTGD-5403-17 TOXIC GAS |  |  |  | DETECTOR- NEAR MANIFOLD
45 | 11-18-XTGD-5403-18 TOXIC GAS |  |  |  | DETECTOR- NEAR C02
ANALYSER | AL-0100-01
46 | 11-18-XTGD-5403-19 TOXIC GAS |  |  |  | DETECTOR- NEAR C02
ANALYSER | AL-0100-02
47 | 11-18-XTG D-5403-20 TOXIC |  |  |  | GAS DETECTOR-ISOLATION VALVE
48 | 44-76-XTGD-5401-01 TOXIC GAS |  |  |  | DETECTOR- RUMAITHA TIE IN
49 | 44-76-XTG D-5401-02 TOXIC |  |  |  | GAS DETECTOR- RUMAITHA TIE IN
50 | 44-76-XTGD-5401-05 TOXIC GAS |  |  |  | DETECTOR- RUMAITHA TIE IN
51 | 44- 76-XTG D-5401-06 |  |  |  | TOXIC GAS DETECTOR- RUMAITHA TIE IN
4 | DOCUMENT TITLE: Project No.: P11569
11.99.40.2619
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S REV. 1 GAS DETECTOR Date: 06-08-2015
� | tuco TYCO DOC. |  |  |  | NO.: TFS-D- CA150270-007 REV.3
52 | 44- 76-XTG D-5401-0 |  |  |  | 7 TOXIC GAS DETECTOR- RUMAITHA TIE IN
53 | 44-76-XTGD-5401-08 TOXIC GAS |  |  |  | DETECTOR- RUMAITHA TIE IN
11.99.40.2619 | Project No.: P11569
INSTRUMENT | DATA SHEET FOR |  |  |  | H2S
MODE� | S4000TH
H2S | Gas Detection
The | Model S4000TH Intelligent Sensor is a
All | of the S4000TH electronics are contained within an
explosion-proof | housing so that |  |  |  | sensor information can
detection | range at the sensor. In addition, the S4000TH
The | S4000TH includes a three (3) digit LED display.
and | eight fault codes. The S4000TH has four different operating modes. First,
Selecting | Setup Mode on the S4000TH is accomplished
MOOE� | S4000TH
United | Kingdom, SK11 OLR
housing, | push terminals) 3 |  |  |  | wire shielded cable. Max. distance
between | S4000TH and power
247 | units with repeaters Complies with EN50270,
(optional) | Baud Rate: RS-485 Output:
Aluminum | 6061-T6 alloy (cover),
A356-T6 | alloy (base) or
IIB+H2, | T6, Type 4X
Ex | d IIB+H2. TS Gb IP66
Range: | -S8°F to 185°F (-50°C to 85°C)
Publication#: | DS-S4000TH-E1212e
MODEL | S4000TH
MODEL | S4000TH
• | (Std) S4000TH HYDROGEN SULFIDE INTELLIGENT SENSOR
A. | RELA YS1-NC:
9-o | 4·20MA OUTPUT. WITH RELAYS. WITH DUAL MODBUS with S4000T Modbus unit !}'.ee
8. | RELAY-STATE-NC:
1-r,, | LATCH ALARM/NON-LATCH WARN DE-ENERGIZED
2-o | LATCH ALARM/NON-LATCH WARN ENGERGIZED
3-o | LATCH ALARM/LATCH WARN DE-ENERGIZED
5- | . NON-LATCH ALARM/NON-LATCH WARN DE-ENERGIZED
6-o | NON-LATCH ALARM/NON-LATCH WARN ENERGIZED
r-« | NON-LATCH ALARM/LATCH WARN DE-ENERGIZED
8-o | NON-LATCH ALARM/LATCH WARN ENERGIZED
C. | H2S-SENSOR:
01-u | (Std) 50445-1 SENSOR Al OTO 100 PPM H2S
02-o | 50445-5 SENSOR Al OTO 50 PPM H2S
03-o | 50445-9 SENSOR Al OTO 20 PPM H2S
04-o | 50448-1 SENSOR SS OTO 100 PPM H2S
05-o | 50448-5 SENSOR SS OTO 50 PPM H2S
06-o | 50448·9 SENSOR SS O TO 20 PPM H2S
11-o | 51457-ll SENSOR SS ATEX H2S 0-100 (WILUGS)
12- | 51457-SL SENSOR SS ATEX H2S 0-50 (W/LUGS)
13-o | 51457·9L SENSOR SS ATEX H2S 0-20 (W/LUGS)
1·o | (Std) ATEX/CSA-English
3·.:i | ATEX/CSA·ENGLISH--SCREW TERMINAL
5-o | GMI-GMIUSST HOUSING
6- | GMI-GMIL/SST HOUSING SCREW |  |  |  | TERMINALS